# Air Circuit Breaker Test Form – Part A

# Building Details

| Building ID | Location |
| --- | --- |
| Date | Testing Contractor | Testing Technician |

# Circuit Breaker Data

| Cell |  |  | Poles |  |
| --- | --- | --- | --- | --- |
| Manufacturer |  |  | Rated Frequency |  |
| Type |  |  | BIL KV |  |
| Serial No. |  |  | Inter Cap (KA) |  |
| Rated Amps |  |  | Close CCT (V) |  |
| Rated Volts |  |  | Trip CCT (V) |  |

# Circuit Breaker Inspection

| Item | Yes | No | Comments |
| --- | --- | --- | --- |
| Contacts |  |  |  |
| Shutter |  |  |  |
| Auxiliary Contacts |  |  |  |
| Control Fuses |  |  |  |
| Control Wiring |  |  |  |
| Status Indicator |  |  |  |
| Position Indicators |  |  |  |
| Control Interlocks |  |  |  |
| Operation Counter |  |  |  |
| Arc Chutes |  |  |  |
| Barriers |  |  |  |
| Alignment |  |  |  |
| Tighten Bolts |  |  |  |
| Blown Fuse Indictor |  |  |  |
| Dirt Accumulation |  |  |  |
| Corrosion |  |  |  |

# Meter Verification

| Designation | Manufacturer | Type | Scale | Test I/P | Reading |
| --- | --- | --- | --- | --- | --- |

# Air Circuit Breaker Test Form – Part B

# Contact Resistance Test

| Test Amps |  |  |  | Microhms |
| --- | --- | --- | --- | --- |
| Equipment Used |  |  |  | A | B | C |
| Comments: |  |  | Initial |  |  |  |
|  |  | Cleaned |  |  |  |

# Insulation Resistance Test

| Equipment Used |  |  | KV | Time | A | B | C |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sec |  | Min |  |  |  |  |  |  |  |
| Megohm |  | Microamp |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |

# Function Test

| Breaker Position | Charge | Close | Trip | Trip Relay |
| --- | --- | --- | --- | --- |
|  | Manual | Electric | Manual | Electric | Manual | Electric |  |
| Connected |  |  |  |  |  |  |  |
| Test |  |  |  |  |  |  |  |
| Disconnected |  |  |  |  |  |  |  |
| Removed |  |  |  |  |  |  |  |
| Comments: |  |

Add additional Test Form sheets as required

# Air Circuit Breaker Test Form – Part C

# DC Hipot Test

# Type of Test	Test Conditions

| Acceptance |  |  | Temperature ((C) |  |
| --- | --- | --- | --- | --- |
| Maintenance |  |  | Humidity (%) |  |

# DC Hipot Test Data

| Test KV |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Time (minutes) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Leakage A ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Leakage B ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Leakage C ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Sketch | Graph |
| --- | --- |

Notes

Add additional Test Form sheets as required

# Disconnect Switch Test Form – Part A

# Building Details

| Building ID | Location |
| --- | --- |
| Date | Testing Contractor | Testing Technician |

# Disconnect Switch Data

| Cell |  |  | Poles |  |
| --- | --- | --- | --- | --- |
| Manufacturer |  |  | Rated Frequency |  |
| Type |  |  | BIL KV |  |
| Serial No. |  |  | Inter Cap (KA) |  |
| Rated Amps |  |  | Temp (ºC) |  |
| Rated Volts |  |  | Humidity (%) |  |

# Disconnect Switch Inspection

| Item | Yes | No | Comments |
| --- | --- | --- | --- |
| Contacts |  |  |  |
| Control Wiring |  |  |  |
| Key Interlocks |  |  |  |
| Operation Counter |  |  |  |
| Barriers |  |  |  |
| Alignment |  |  |  |
| Tighten Bolts |  |  |  |
| Dirt Accumulation |  |  |  |
| Corrosion |  |  |  |

# Meter Verification

| Designation | Manufacturer | Type | Scale | Test I/P | Reading |
| --- | --- | --- | --- | --- | --- |

# Disconnect Switch Test Form – Part B

# Insulation Resistance Test

| Equipment Used |  |  | KV | Time | A | B | C |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sec |  | Min |  |  |  |  |  |  |  |
| Megohm |  | Microamp |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |

# Contact Resistance Test

| Test Amps |  |  |  | Microhms |
| --- | --- | --- | --- | --- |
| Equipment Used |  |  |  | A | B | C |
| Comments: |  |  | Initial |  |  |  |
|  |  | Cleaned |  |  |  |

# Function Test

|  | N/A | OK | Not OK | Comments |
| --- | --- | --- | --- | --- |
| Close |  |  |  |  |
| Open |  |  |  |  |
| Drive Motor |  |  |  |  |
| Drive Linkage |  |  |  |  |
| Remote Control |  |  |  |  |

| Comments |  |
| --- | --- |

Add additional Test Form sheets as required

# Disconnect Switch Test Form – Part C

# DC Hipot Test Data

| Test KV |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Time (minutes) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Sketch | Graph |
| --- | --- |

| Notes |  |
| --- | --- |

Add additional Test Form sheets as required

# Dry Type Transformer Test Form – Part A

# Building Details

| Building ID | Location |
| --- | --- |
| Date | Testing Contractor | Testing Technician |

# Transformer Data

| Designation |  |  | Manufacturer |  |
| --- | --- | --- | --- | --- |
| Type |  |  | Serial Number |  |
| KVA |  |  | BIL Rating |  |
| Primary Volts |  |  | Weight |  |
| Secondary Volts |  |  | % Impedance |  |
| Amps Primary |  |  | Insulation Class |  |
| Amps Secondary |  |  | No. of Taps |  |
| Year |  |  | Temp Rise (ºC) |  |

# Transformer Inspection

| Item | Yes | No | Comments |
| --- | --- | --- | --- |
| Paint |  |  |  |
| Fuses |  |  |  |
| Dirt |  |  |  |
| Corrosion |  |  |  |
| Corona |  |  |  |
| Bushings |  |  |  |
| Insulators |  |  |  |
| Primary Connection |  |  |  |
| Secondary Connection |  |  |  |
| Grounding |  |  |  |
| Ground Resistor |  |  |  |
| Clearance |  |  |  |
| Doors/Covers |  |  |  |
| Windings |  |  |  |
| Mounting Hardware |  |  |  |
| Control Wiring |  |  |  |
| Control Relays |  |  |  |
| Voltage Regulator |  |  |  |
| Tap Changer |  |  |  |
| Bolt Torque |  |  |  |

| Notes |  |
| --- | --- |

# Dry Type Transformer Test Form – Part B

# Insulation Power Factor Test

| Primary to Secondary & Ground |  | Secondary to Primary & Ground |
| --- | --- | --- |
| Capacitance (pF) |  |  | Capacitance (pF) |  |
| Dissipat. Factor (%) |  |  | Dissipat. Factor (%) |  |
| Ambient Temperature ((C) |  |  | Comments: |
| Winding Temperature ((C) |  |  |  |
| Humidity (%) |  |  |  |
| Equipment Used |  |  |  |

Ratio Test

| Tap Position | Primary Volts | Calc. Ratios | Measured Ratio | Factory Ratio |
| --- | --- | --- | --- | --- |
|  |  |  | A | B | C | A | B | C |

# DC Insulation Resistance Test

| Primary to Secondary | Primary/Secondary to Ground | Secondary/Primary to Ground |
| --- | --- | --- |
| Kv | Time | (amp | Meg( | Kv | Time | (amp | Meg( | Kv | Time | (amp | Meg( |

# Type of Test	Test Time

| Acceptance |  |  | Minutes |  |
| --- | --- | --- | --- | --- |
| Maintenance |  |  | Seconds |  |
| Equipment Used |  |

| Comments |  |
| --- | --- |

Add additional Test Form sheets as required

# Dry Type Transformer Test Form – Part C

# DC Hipot Test

| Test KV |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Time (minutes) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Sketch | Graph |
| --- | --- |

| Notes |  |
| --- | --- |

# Core Ground Test - 250V Megger Test

| Continuity |  | Yes |  |  | No |  |
| --- | --- | --- | --- | --- | --- | --- |
| Results Acceptable |  | Yes |  |  | No |  |

| Comments |  |
| --- | --- |

Add additional Test Form sheets as required

# Power Transformer (Liquid Filled) Test Form – Part A

# Building Details

| Building ID | Location |
| --- | --- |
| Date | Testing Contractor | Testing Technician |

# Transformer Data

| Designation |  |  | Manufacturer |  |
| --- | --- | --- | --- | --- |
| Type |  |  | Serial Number |  |
| KVA |  |  | BIL Rating |  |
| Primary Volts |  |  | Weight |  |
| Secondary Volts |  |  | % Impedance |  |
| Amps Primary |  |  | Insulation Class |  |
| Amps Secondary |  |  | No. of Taps |  |
| Year |  |  | Temp Rise (ºC) |  |

# Transformer Inspection

| Item | Yes | No | Comments |
| --- | --- | --- | --- |
| Paint |  |  |  |
| Fuses |  |  |  |
| Dirt |  |  |  |
| Corrosion |  |  |  |
| Corona |  |  |  |
| Bushings |  |  |  |
| Insulators |  |  |  |
| Primary Connection |  |  |  |
| Secondary Connection |  |  |  |
| Grounding |  |  |  |
| Ground Resistor |  |  |  |
| Clearance |  |  |  |
| Doors/Covers |  |  |  |
| Windings |  |  |  |
| Mounting Hardware |  |  |  |
| Control Wiring |  |  |  |
| Control Relays |  |  |  |
| Voltage Regulator |  |  |  |
| Tap Changer |  |  |  |
| Bolt Torque |  |  |  |

# Gauges

| Oil Level |  |  |  |
| --- | --- | --- | --- |
| Oil Temperature |  |  |  |
| Gas Pressure |  |  |  |
| Winding Temp (ºC) |  |  |  |

# Alarms

| Oil Level |  |  |  |
| --- | --- | --- | --- |
| Oil Temperature |  |  |  |
| Gas Pressure |  |  |  |
| Winding Temp (ºC) |  |  |  |

# Power Transformer (Liquid Filled) Test Form – Part B

# Insulation Power Factor Test

| Primary to Secondary & Ground |  | Secondary to Primary & Ground |
| --- | --- | --- |
| Capacitance (pF) |  |  | Capacitance (pF) |  |
| Dissipat. Factor (%) |  |  | Dissipat. Factor (%) |  |
| Ambient Temperature ((C) |  |  | Comments: |
| Winding Temperature ((C) |  |  |  |
| Humidity (%) |  |  |  |
| Equipment Used |  |  |  |

Ratio Test

| Tap Position | Primary Volts | Calc. Ratios | Measured Ratio | Factory Ratio |
| --- | --- | --- | --- | --- |
|  |  |  | A | B | C | A | B | C |

| 12 |  |  | 120 |  |
| --- | --- | --- | --- | --- |

| Tap Found |  |  | Tap Left |  |
| --- | --- | --- | --- | --- |
| Equipment Used |  |

# DC Insulation Resistance Test

| Primary to Secondary | Primary/Secondary to Ground | Secondary/Primary to Ground |
| --- | --- | --- |
| Kv | Time | (amp | Meg( | Kv | Time | (amp | Meg( | Kv | Time | (amp | Meg( |

# Type of Test	Test Time

| Acceptance |  |  | Minutes |  |
| --- | --- | --- | --- | --- |
| Maintenance |  |  | Seconds |  |

| Equipment Used |  |
| --- | --- |
| Comments |  |

Add additional Test Form sheets as required

# Power Transformer (Liquid Filled) Test Form – Part C

# Liquid Dielectric Strength Test

| Ambient Temp. ((C) |  |  | Tank Type: | Sealed |  | Conservator |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Liquid Temp. ((C) |  |  |  |  |  |
| Tank Pressure |  |  | Sample Taken: | Top |  |
| Date Sampled |  |  |  | Bottom |  |
| Date Tested |  |  |  | Valve |  |
| Tested By |  |  | Thief |  |

| Test Sample No. 1 |  | Test Sample No. 2 |
| --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 |  | 1 | 2 | 3 | 4 | 5 |

|  | Yes | No |
| --- | --- | --- |
| Average Dielectric Strength (KV) |  |  | Acceptable |  |  |

| Sample Color |  | Chemical Analysis |
| --- | --- | --- |
| Straw White |  |  | Moisture Content (ppm) |  |
| Straw Yellow |  |  | Acid Content (mg Of KOH per gm) |  |
| Lemon Yellow |  |  | PCB Content (ppm) |  |
| Orange |  |  |  |  |
| Reddish Orange |  |  |  |  |
| Brown |  |  |  |  |
| Black |  |  |  |  |

| Core Ground Test |  |
| --- | --- |

| Comments |  |
| --- | --- |

# Power Transformer (Liquid Filled) Test Form – Part D

# Oil, Chemical & Gas Analysis

| Sample Point |  |  | Fluid Level |  |
| --- | --- | --- | --- | --- |
| Sample Number |  |  | Air Temperature ((C) |  |
| Year in Service |  |  | Liquid Temperature ((C) |  |

| Test Performed | Accept Values | Results Test 1 | Results Test 2 | Comments |
| --- | --- | --- | --- | --- |
| Liquid Dielectric Test |
| ASTM D877 |  |  |  |  |
| Chemical Analysis |
| Moisture Content |  |  |  |  |
| Neutralization No. |  |  |  |  |
| Interfacial Tension |  |  |  |  |
| Colour |  |  |  |  |
| Gas Analysis |
| Hydrogen (H2) |  |  |  |  |
| (O2+A)/(N2) |  |  |  |  |
| Carbon Monoxide (CO) |  |  |  |  |
| Methane (CH4) |  |  |  |  |
| Carbon Dioxide (CO2) |  |  |  |  |
| Ethylene (C2H4) |  |  |  |  |
| Ethane (C2H) |  |  |  |  |
| Acetylene (C2H2) |  |  |  |  |
| Combustible |  |  |  |  |
| Total Gas Content |  |  |  |  |
| CO/CO2 |  |  |  |  |

# Core Ground Test – 250V Megger Test

|  | Yes | No |
| --- | --- | --- |
| Continuity |  |  |
| Results Acceptable |  |  |

| Comments |  |
| --- | --- |

# Oil Circuit Breaker Test Form – Part A

# Building Details

| Building ID | Location |
| --- | --- |
| Date | Testing Contractor | Testing Technician |

# Circuit Breaker Data

| Cell |  |  | Poles |  |
| --- | --- | --- | --- | --- |
| Manufacturer |  |  | Rated Frequency |  |
| Type |  |  | BIL KV |  |
| Serial No. |  |  | Inter Cap (KA) |  |
| Rated Amps |  |  | Close CCT (V) |  |
| Rated Volts |  |  | Trip CCT (V) |  |

# Circuit Breaker Inspection

| Item | Yes | No | Comments |
| --- | --- | --- | --- |
| Contacts |  |  |  |
| Shutter |  |  |  |
| Auxiliary Contacts |  |  |  |
| Control Fuses |  |  |  |
| Control Wiring |  |  |  |
| Status Indicator |  |  |  |
| Position Indicators |  |  |  |
| Control Interlocks |  |  |  |
| Operation Counter |  |  |  |
| Arc Chutes |  |  |  |
| Barriers |  |  |  |
| Alignment |  |  |  |
| Tighten Bolts |  |  |  |
| Blown Fuse Indictor |  |  |  |
| Dirt Accumulation |  |  |  |
| Corrosion |  |  |  |

# Meter Verification

| Designation | Manufacturer | Type | Scale | Test I/P | Reading |
| --- | --- | --- | --- | --- | --- |

# Oil Circuit Breaker Test Form – Part B

# Contact Resistance Test

| Test Amps |  |  |  | Microhms |
| --- | --- | --- | --- | --- |
| Equipment Used |  |  |  | A | B | C |
| Comments: |  |  | Initial |  |  |  |
|  |  | Cleaned |  |  |  |

# Insulation Resistance Test

| Equipment Used |  |  | KV | Time | A | B | C |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sec |  | Min |  |  |  |  |  |  |  |
| Megohm |  | Microamp |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |

# Function Test

| Breaker Position | Charge | Close | Trip | Trip Relay |
| --- | --- | --- | --- | --- |
|  | Manual | Electric | Manual | Electric | Manual | Electric |  |
| Connected |  |  |  |  |  |  |  |
| Test |  |  |  |  |  |  |  |
| Disconnected |  |  |  |  |  |  |  |
| Removed |  |  |  |  |  |  |  |
| Comments |  |

Add additional Test Form sheets as required

# Oil Circuit Breaker Test Form – Part C

# Liquid Dielectric Strength Test

| Ambient Temp. ((C) |  |  | Tank Type: | Sealed |  | Conservator |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Liquid Temp. ((C) |  |  |  |  |  |
| Tank Pressure |  |  | Sample Taken: | Top |  |
| Date Sampled |  |  |  | Bottom |  |
| Date Tested |  |  |  | Valve |  |
| Tested By |  |  | Thief |  |

| Test Sample No. 1 |  | Test Sample No. 2 |
| --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 |  | 1 | 2 | 3 | 4 | 5 |

|  | Yes | No |
| --- | --- | --- |
| Average Dielectric Strength (KV) |  |  | Acceptable |  |  |

| Sample Color |  | Chemical Analysis |
| --- | --- | --- |
| Straw White |  |  | Moisture Content (ppm) |  |
| Straw Yellow |  |  | Acid Content (mg Of KOH per gm) |  |
| Lemon Yellow |  |  | PCB Content (ppm) |  |
| Orange |  |  |  |  |
| Reddish Orange |  |  |  |  |
| Brown |  |  |  |  |
| Black |  |  |  |  |

| Core Ground Test |  |
| --- | --- |

| Comments |  |
| --- | --- |

Add additional Test Form sheets as required

# Oil Circuit Breaker Test Form – Part D

# Oil, Chemical & Gas Analysis

| Sample Point |  |  | Fluid Level |  |
| --- | --- | --- | --- | --- |
| Sample Number |  |  | Air Temperature ((C) |  |
| Year in Service |  |  | Liquid Temperature ((C) |  |

| Test Performed | Accept Values | Results Test 1 | Results Test 2 | Comments |
| --- | --- | --- | --- | --- |
| Liquid Dielectric Test |
| ASTM D877 |  |  |  |  |
| Chemical Analysis |
| Moisture Content |  |  |  |  |
| Neutralization No. |  |  |  |  |
| Interfacial Tension |  |  |  |  |
| Colour |  |  |  |  |
| Gas Analysis |
| Hydrogen (H2) |  |  |  |  |
| (O2+A)/(N2) |  |  |  |  |
| Carbon Monoxide (CO) |  |  |  |  |
| Methane (CH4) |  |  |  |  |
| Carbon Dioxide (CO2) |  |  |  |  |
| Ethylene (C2H4) |  |  |  |  |
| Ethane (C2H) |  |  |  |  |
| Acetylene (C2H2) |  |  |  |  |
| Combustible |  |  |  |  |
| Total Gas Content |  |  |  |  |
| CO/CO2 |  |  |  |  |

# Overhead Radial Power Line Test Form

# Building Details

| Site No. | Location |
| --- | --- |
| Date | Testing Contractor | Testing Technician |

# Power Line Data

| Pole No. |  |  | Location |  |
| --- | --- | --- | --- | --- |
| Age |  |  | System Voltage |  |

| Devices on Pole |  |
| --- | --- |

# Power Pole Inspection

| Item Check | Yes | No | Comments |
| --- | --- | --- | --- |
| Visually Inspect Poles |  |  |  |
| Sound Test Poles |  |  |  |
| Crossarms |  |  |  |
| Bolts |  |  |  |
| Rack Assemblies |  |  |  |
| Guys |  |  |  |
| Guy Wires |  |  |  |
| Dead Ends |  |  |  |
| Insulators |  |  |  |
| Grounding |  |  |  |
| Ground Resistors |  |  |  |
| Clearances |  |  |  |
| Connections |  |  |  |
| Deterioration |  |  |  |
| Metal Fatigue |  |  |  |

| Notes |  |
| --- | --- |

# Power Cables Test Form

# Building Details

| Building ID | Location |
| --- | --- |
| Date | Testing Contractor | Testing Technician |

# Cable Data

| Cable No. or Designation |  |  | Length |  |
| --- | --- | --- | --- | --- |
| Type |  |  | Manufacturer |  |
| Size |  |  | Operating Voltage |  |
| Insulation Type |  |  | Test Voltage Applied |  |
| Amps |  |  | Terminations |  |
| Number of Cond/Phase |  |  | Shield |  |
| Splices |  |  |  |  |

# Type of Test	Test Conditions

| Acceptance |  |  | Temperature ((C) |  |
| --- | --- | --- | --- | --- |
| Maintenance |  |  | Humidity (%) |  |

# DC Hipot Test Data

| Test KV |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Time (minutes) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Leakage A ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Leakage B ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Leakage C ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Sketch | Graph |
| --- | --- |

Notes:

Add additional Test Form sheets as required

# Protective Relays Test Form

# Building Details

| Building ID | Location |
| --- | --- |
| Date | Testing Contractor | Testing Technician |

# Relay Data

| Designation |  |
| --- | --- |
| Type |  |  | Model No. |  |
| Device Serial No. |  |  | Manufacturer |  |

# Trip Settings as Found

| Pick Up Amps |  |  | Time (cycles) |  |
| --- | --- | --- | --- | --- |
| Pick Up Amps Range |  |  | Time (cycles) Range |  |

| Restraint: | Transmit Only |  | Transmit and Receive |  | None |  |
| --- | --- | --- | --- | --- | --- | --- |

Calibration Test

| Using Primary Current Injection |  |  | Using Secondary Current Injection |  |
| --- | --- | --- | --- | --- |

|  | Pick Up Test: |  |  | Pick Up Test: |  |  | As Left |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Set at P.U. Volts at |  | Amps |  |  | Volts |  |  | Volts |
| Set at P.U. Volts at |  | Amps |  |  | Volts |  |  | Volts |
| Set at P.U. Volts at |  | Amps |  |  | Volts |  |  | Volts |

Time Test

| Pick Up Set at |  | Amps |  | Time (Cycles) Set at |  | = |  | Seconds |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Set P.U Volts at |  | Volts = Time to Trip = |  | Seconds |
| --- | --- | --- | --- | --- |
| Set P.U Volts at |  | Volts = Time to Trip = |  | Seconds |
| Set P.U Volts at |  | Volts = Time to Trip = |  | Seconds |

| Operational Test: |  |
| --- | --- |
| Restraint Out Test |  | Volts DC |

|  | OK | Not OK |  |  | OK | Not OK |
| --- | --- | --- | --- | --- | --- | --- |
| Time Restraint Test |  |  |  | Current Sensor Size |  |  |
| Transmitter Unit Test |  |  |  | Current Sensor Checks |  |  |
| System Coordination Testing |  |  |  | Circuit Breaker Trip Tested |  |  |
| Restraint Continuity Test |  |  |  |  |  |  |

Notes:

# Surge Arrestor Test Form

# Building Details

| Building ID | Location |
| --- | --- |
| Date | Testing Contractor | Testing Technician |

# Surge Arrestor Data

| Designation |  |
| --- | --- |
| Type |  |  | Manufacturer |  |
| Insulation Type |  |  | Operating Voltage |  |
| Amps |  |  | Test Voltage Applied |  |

# Insulation Resistance Test

| Equipment Used |  |  | KV | Time | A | B | C |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sec |  | Min |  |  |  |  |  |  |  |
| Megohm |  | Microamp |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |

# Surge Arrestor Inspection

| Item Check | Yes | No | Comments |
| --- | --- | --- | --- |
| Cleanliness |  |  |  |
| Cracks |  |  |  |
| Chips |  |  |  |
| Tracking |  |  |  |

| Grounding Continuity Test: Acceptable |  | Yes |  |  | No |  |
| --- | --- | --- | --- | --- | --- | --- |

| Notes |  |
| --- | --- |

Add additional Test Form sheets as required

# Switch Gear Test Form – Part A

# Building Details

| Building ID | Location |
| --- | --- |
| Date | Testing Contractor | Testing Technician |

# Switch Gear Data

| Manufacturer |  |  | Rated Frequency |  |
| --- | --- | --- | --- | --- |
| Type |  |  | BIL (KV) |  |
| Serial No. |  |  | Bus Bracing (KA) |  |
| Rated Amps |  |  | No. of Sections |  |
| Rated Volts |  |  |  |  |

# Cell Designation

| Cell | Description |  | Cell | Description |
| --- | --- | --- | --- | --- |

# Sketch of Cell Layout

| Notes |  |
| --- | --- |

# Switch Gear Test Form - Part B

| Insulation Test - Time: |  | Insulation Test - Values: |
| --- | --- | --- |
| Seconds | Minutes |  | Megohms | Microamps |

| KV | Time | A | B | C |  | Bus Section |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Lightning Arrestors |  |
|  |  |  |  |  |  |  | N/A |  | Conn |  | Disc |
|  |  |  |  |  |  | Comments: |

| KV | Time | A | B | C |  | Bus Section |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Lightning Arrestors |  |
|  |  |  |  |  |  |  | N/A |  | Conn |  | Disc |
|  |  |  |  |  |  | Comments: |

| KV | Time | A | B | C |  | Bus Section |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Lightning Arrestors |  |
|  |  |  |  |  |  |  | N/A |  | Conn |  | Disc |
|  |  |  |  |  |  | Comments: |

| Notes |  |
| --- | --- |

# Switch Gear Test Form - Part C

Contact Resistance Test (Microhms)

| From Cell No. | To Cell No. | Phase A | Phase B | Phase C | N | Comments |
| --- | --- | --- | --- | --- | --- | --- |

| Notes |  |
| --- | --- |

Add additional Test Form sheets as required

# Switch Gear Test Form - Part D

Contact Resistance Test (Microhms)

| From Cell No. | To Cell No. | Phase A | Phase B | Phase C | N | Comments |
| --- | --- | --- | --- | --- | --- | --- |

| Notes |  |
| --- | --- |

Add additional Test Form sheets as required

| Equipment | Make | Model | Quantity |
| --- | --- | --- | --- |
| Power Transformer, Dry Type |  |  |  |
| Power Transformer, Liquid Filled |  |  |  |
| Switchgear Enclosure |  |  |  |
| High Voltage Air Circuit Breakers |  |  |  |
| High Voltage Oil Circuit Breakers |  |  |  |
| Fused LB Disconnect Switchgear |  |  |  |
| Unfused LB Disconnect Switchgear |  |  |  |
| Fused NLB Disconnect Switchgear |  |  |  |
| Unfused NLB Disconnect Switchgear |  |  |  |
| Induction Disc Relays |  |  |  |
| Overcurrent Relays |  |  |  |
| Solid State Relays |  |  |  |
| Overhead Power Line Insulators |  |  |  |
| Overhead Power Line Connectors |  |  |  |
| Overhead Power Line Wooden Poles |  |  |  |
| Overhead Power Line Metal Tower Structure |  |  |  |
| Surge Arresors |  |  |  |