Section Cover Page

Section 16784 2005-02-08 Closed Circuit TV Maintenance

Use this Section to specify Maintenance Service requirements for closed circuit television maintenance.

This Master Specification contains:

.1	This Cover Page

.2	Specification Section Text:

1.	General

1.1	Section Includes

1.2	Related Services Not Provided

1.3	Related Requirements

1.4	Operation and Maintenance Data

1.5	Inspection Report

2.	Products

2.1	Materials

2.2	Replacement Parts

3.	Execution

3.1	Examination

3.2	Adjustment and Operations Tests

Section 16784A	Closed Circuit TV Systems Inspection Report

Section 16784B	Closed Circuit TV Monitor Inspection Report

Section 16784C	Closed Circuit TV Camera Maintenance Inspection Report

EDITING:  Use this Section as is:  Do not modify in any way.

1.	General

1.1	section includes

.1	This Section includes maintenance requirements for Closed Circuit T.V. including cleaning adjustment and general inspection requirements only.

1.2	related services not provided

.1	Repair or replacement services of faulty or non-operating components is not included in this Section.

1.3	related requirements

.1	Refer to Closed Circuit T.V. Maintenance Materials and Equipment Schedule; and Closed Circuit T.V. Maintenance Schedule for:

.1	materials and equipment to be provided by Minister, and

.2	property locations where services are to be performed.

1.4	operation and maintenance data

.1	Obtain from Minister available operation and maintenance data for Closed Circuit T.V. materials and equipment.

1.5	inspection report

.1	Complete Closed Circuit T.V. Maintenance Inspection Report, appended to this Section and submit to Minister’s Representative.

.2	Report shall include recommendations for repair or replacement of all faulty or non-operating components

2.	Products

2.1	materials

.1	Provide cleaners, supplies and ladders not provided by Minister.

.2	Refer to Closed Circuit T.V. Maintenance Materials, Equipment and Location Schedule for materials and equipment to be provided by Minister.

2.2	replacement parts

.1	Do not include for repairs or replacement of faulty non-operating components or any closed circuit T.V.

3.	EXECUTION

3.1	EXAMINATION

.1	For each closed circuit T.V., inspect, test and report on condition of the applicable components specified in the CCTV inspection report that appends this section.

.2	Inspect camera and monitor mounts.  Remove camera cover and vacuum.  Remove monitor cover and vacuum.  Clean monitor C.R.T. face.  Clean camera lens.

.3	Conduct the following performance tests:

.1	black and white contrast,

.2	image burn,

.3	sharpness,

.4	horizontal and vertical sync,

.5	sequential switching

.6	proper pan,

.7	tilt and zoom,

.8	outdoor housing heater

.9	fan, and

.10	glass face wiper.

3.2	adjustments and operations test

.1	Check and adjust camera position.

.2	Check for frayed or loose coaxial connectors and cable.

.3	Check and adjust auto iris (where applicable).

.4	Check and adjust F stop on lens.

.5	Adjust beam, target and focus (where applicable).

.6	Adjust contrast, brightness, vertical and horizontal hold, on monitor.

.7	Check for image burn on camera and monitor.

.8	Check and adjust pan and tilt.

.9	Check outdoor camera housing components.

.10	Check switcher and controllers

.11	Check and adjust security scanners.

END OF SECTION